## Part 1. Total Demand
Notes:
1. Two year sequence used in sizing to account for carry over storage of water from year 1 to year (same precipitation pattern used for both)
2. Yield is Runoff calculated in Class 15
3. Demand is Indoor + Outdoor Demand calculated in Class 15
4. Cumulative Storage is Yield - Demand for each month added to the storage from the previous month
5. Municipal Makeup is the amount of water that must be supplied from the piped-in municipal supply to meet the deficit
Year 1
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 | 13838.152 | -13127.552 | 13127.552
February | 3197.7 | 12498.976 | -9301.276 | 9301.276
March | 2013.3667 | 13838.152 | -11824.7853 | 11824.7853
April | 3316.1333 | 13391.76 | -10075.6267 | 10075.6267
May | 1302.7667 | 51008.2993 | -49705.5326 | 49705.5326
June | 2131.8 | 60558.7763 | -58426.9763 | 58426.9763
July | 22265.4667 | 37924.7585 | -15659.2918 | 15659.2918
August | 33516.6333 | 30106.8581 | 3409.7752 | 0
September | 6158.5333 | 26834.1209 | -17265.8123 | 17265.8123
October | 2605.5333 | 13838.152 | -11232.6187 | 11232.6187
November | 1065.9 | 13391.76 | -12325.86 | 12325.86
December | 1065.9 | 13838.152 | -12772.252 | 12772.252
Year 2
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 | 13838.152 | -13127.552 | 13127.552
February | 3197.7 | 12498.976 | -9301.276 | 9301.276
March | 2013.3667 | 13838.152 | -11824.7853 | 11824.7853
April | 3316.1333 | 13391.76 | -10075.6267 | 10075.6267
May | 1302.7667 | 51008.2993 | -49705.5326 | 49705.5326
June | 2131.8 | 60558.7763 | -58426.9763 | 58426.9763
July | 22265.4667 | 37924.7585 | -15659.2918 | 15659.2918
August | 33516.6333 | 30106.8581 | 3409.7752 | 0
September | 6158.5333 | 26834.1209 | -17265.8123 | 17265.8123
October | 2605.5333 | 13838.152 | -11232.6187 | 11232.6187
November | 1065.9 | 13391.76 | -12325.86 | 12325.86
December | 1065.9 | 13838.152 | -12772.252 | 12772.252
Totals | 79350.3333 | 301067.9171 |  | 221717.5837
Cistern Size
Maximum Demand | 3409.7752 | gal
| 455.5478 | cu. Ft
21.3436

## Part 2. Indoor Demand Only
Notes:
1. Two year sequence used in sizing to account for carry over storage of water from year 1 to year (same precipitation pattern used for both)
2. Yield is Runoff calculated in Unit 5
3. Demand is Indoor + Outdoor Demand calculated in Unit 5
4. Cumulative Storage is Yield - Demand for each month added to the storage from the previous month
5. Municipal Makeup is the amount of water that must be supplied from the piped-in municipal supply to meet the deficit
Year 1
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 | 13838.152 | -13127.552 | 13127.552
February | 3197.7 | 12498.976 | -9301.276 | 9301.276
March | 2013.3667 | 13838.152 | -11824.7853 | 11824.7853
April | 3316.1333 | 13391.76 | -10075.6267 | 10075.6267
May | 1302.7667 | 13838.152 | -12535.3853 | 12535.3853
June | 2131.8 | 13391.76 | -11259.96 | 11259.96
July | 22265.4667 | 13838.152 | 8427.3147 | 0
August | 33516.6333 | 13838.152 | 28105.796 | 0
September | 6158.5333 | 13391.76 | 20872.5693 | 0
October | 2605.5333 | 13838.152 | 9639.9507 | 0
November | 1065.9 | 13391.76 | -2685.9093 | 2685.9093
December | 1065.9 | 13838.152 | -12772.252 | 12772.252
Year 2
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 | 13838.152 | -13127.552 | 13127.552
February | 3197.7 | 12498.976 | -9301.276 | 9301.276
March | 2013.3667 | 13838.152 | -11824.7853 | 11824.7853
April | 3316.1333 | 13391.76 | -10075.6267 | 10075.6267
May | 1302.7667 | 13838.152 | -12535.3853 | 12535.3853
June | 2131.8 | 13391.76 | -11259.96 | 11259.96
July | 22265.4667 | 13838.152 | 8427.3147 | 0
August | 33516.6333 | 13838.152 | 28105.796 | 0
September | 6158.5333 | 13391.76 | 20872.5693 | 0
October | 2605.5333 | 13838.152 | 9639.9507 | 0
November | 1065.9 | 13391.76 | -2685.9093 | 2685.9093
December | 1065.9 | 13838.152 | -12772.252 | 12772.252
Totals | 79350.3333 | 162933.08 |  | 83582.7467
Cistern Size
Maximum Demand | 28105.796 | gal
| 3754.9494 | cu. Ft
61.2776
Size | 20*20*9 | cu. Ft
| Not reasonable |  |  | 3500 | -254.9494

## Part 2. Outdoor Demand Only
Notes:
1. Two year sequence used in sizing to account for carry over storage of water from year 1 to year (same precipitation pattern used for both)
2. Yield is Runoff calculated in Unit 5
3. Demand is Indoor + Outdoor Demand calculated in Unit 5
4. Cumulative Storage is Yield - Demand for each month added to the storage from the previous month
5. Municipal Makeup is the amount of water that must be supplied from the piped-in municipal supply to meet the deficit
Year 1
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 |  | 710.6 | 0
February | 3197.7 |  | 3908.3 | 0
March | 2013.3667 |  | 5921.6667 | 0
April | 3316.1333 |  | 9237.8 | 0
May | 1302.7667 | 37170.1473 | -26629.5806 | 26629.5806
June | 2131.8 | 47167.0163 | -45035.2163 | 45035.2163
July | 22265.4667 | 24086.6065 | -1821.1398 | 1821.1398
August | 33516.6333 | 16268.7061 | 17247.9272 | 0
September | 6158.5333 | 13442.3609 | 9964.0997 | 0
October | 2605.5333 |  | 12569.633 | 0
November | 1065.9 |  | 13635.533 | 0
December | 1065.9 |  | 14701.433 | 0
Year 2
Month | Yield | Demand | Cumulative Storage | Municipal Makeup
| (gal) | (gal) | (gal) | (gal)
January | 710.6 | 0 | 15412.033 | 0
February | 3197.7 | 0 | 18609.733 | 0
March | 2013.3667 | 0 | 20623.0997 | 0
April | 3316.1333 | 0 | 23939.233 | 0
May | 1302.7667 | 37170.1473 | -11928.1476 | 11928.1476
June | 2131.8 | 47167.0163 | -45035.2163 | 45035.2163
July | 22265.4667 | 24086.6065 | -1821.1398 | 1821.1398
August | 33516.6333 | 16268.7061 | 17247.9272 | 0
September | 6158.5333 | 13442.3609 | 9964.0997 | 0
October | 2605.5333 | 0 | 12569.633 | 0
November | 1065.9 | 0 | 13635.533 | 0
December | 1065.9 | 0 | 14701.433 | 0
Totals | 79350.3333 | 138134.8371 |  | 58784.5037
Cistern Size
Maximum Demand | 23939.233 | gal
| 3198.2943 | cu. Ft
56.5535
Size | 40*40*9.5 | cu. Ft
| Not reasonable |  |  | 15200 | 12001.7057